{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["监督检验报告信息","Sheet1"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"监督检验报告信息","index":0,"n_rows":10,"n_cols":15,"rows_kept":10,"merged":[[0,0,0,12],[1,0,1,14],[2,0,2,14],[3,0,3,14]],"flags":["formulas_cached_only"]}
["2023年瓶装液化石油气调压器产品质量市监督抽查结果"]
["本次在流通领域抽查了5家单位的5批次产品。\n监督抽查不合格产品检出率为40%。\n依据GB 35844-2018《瓶装液化石油气调压器》标准，对结构[调压器的设定状态、进气口连接和尺寸（手轮外径、手轮宽度）、出气口连接和尺寸（软管连接接头外径）、过流切断安全装置]、气密性、关闭压力、出口压力等4个项目进行了检验。\n抽查发现有 2家企业的2批次产品不符合相关标准要求，不合格项目为：调压器的设定状态、出气口连接和尺寸（软管连接接头外径）、过流切断安全装置、关闭压力、出口压力。我局已依法对不合格产品开始了后处理工作。\n具体抽查结果见附件。\n"]
["附件"]
["2023年瓶装液化石油气调压器产品质量市级监督抽查结果汇总表"]
["序号","产品类别","抽样领域","产品名称","受检单位名称","统一社会信用代码","标称生产者名称","生产日期或批号","规格型号","商标","抽查结果","不合格项目","抽样日期","行政区划","承检单位"]
[1,"家用瓶装液化石油气调压器","流通","家用瓶装液化石油气调压器","莱西市赵秀秀厨具商场","92370285MA3PB51Y38","慈溪市长河北斗星五金配件厂","/","268-A","/","不合格","调压器的设定状态、出气口连接和尺寸（软管连接接头外径）、过流切断安全装置","2023-09-06","莱西市","山东省产品质量检验研究院"]
[2,"家用瓶装液化石油气调压器","流通","瓶装液化石油气调压器","黄岛区利丰盛源厨房设备商店","92370211MA3M0WYN4D","慈溪市长河建辉五金配件厂","2023-06-10","JYT0.6L-A","/","不合格","关闭压力、出口压力","2023-09-07","西海岸新区","山东省产品质量检验研究院"]
[3,"家用瓶装液化石油气调压器","流通","家用瓶装液化石油气调压器","莱西市张成珍炊事用具商场","92370285MA3EHJ7D0L","宁波市鄞州姜山甬金燃具厂","2023-07-27","JYT-0.6L","/","合格","/","2023-09-06","莱西市","山东省产品质量检验研究院"]
[4,"家用瓶装液化石油气调压器","流通","瓶装液化石油气调压器","张志海","92370211MA3E0RBY7B","余姚市万美阀门厂","2023-07","JYT0.6L/B","/","合格","/","2023-09-07","西海岸新区","山东省产品质量检验研究院"]
[5,"家用瓶装液化石油气调压器","流通","瓶装液化石油气调压器","胶南市华尔顿电器经营部","92370211MA3E1YA07J","慈溪市东杰阀门厂","2023-06","JYT-0.6L","/","合格","/","2023-09-07","西海岸新区","山东省产品质量检验研究院"]

{"sheet":"Sheet1","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}